## Calculation
Room | Surface (m²) | m²/person | Persons | Persons | Volume of flow/person | Admission | Surface pipe | Admission Pipes Ø
|  |  |  | (rounding) | (m³/person) | m³/h | (m²) | (mm)
GROUNDFLOOR
ENTREE ACCUEIL | 77.89 | 10 | 7.789 | 7.789 | 45 | 350.505 | 0.032454 | 2x150
HALL REUNION | 44.75 | 10 | 4.475 | 4.475 | 45 | 201.375 | 0.018646 | 2x125
SALLE DE REUNION 1 | 20.55 | 3.5 | 5.8714 | 5.8714 | 45 | 264.2143 | 0.024464 | 200
SALLE DE REUNION 2 | 15.32 | 3.5 | 4.3771 | 5 | 45 | 225 | 0.020833 | 160
SALLE DE REUNION 3 | 24.27 | 3.5 | 6.9343 | 6.9343 | 45 | 312.0429 | 0.028893 | 200
SANIT HOMMES | 6.77 |  |  |  |  | 36 | 0.0033333 | 100
SANIT P.M.R. | 3.11 |  |  |  |  | 36 | 0.0033333 | 100
SANIT DAMES | 6.94 |  |  |  |  | 36 | 0.0033333 | 100
SMALL KITCHENETTE | 2.94 |  |  |  |  | 36 | 0.0033333 | 100
LOCAL POSTE | 14.46 | 10 | 1.446 | 2 | 45 | 90 | 0.0083333 | 125
SALLE DE FORMATION | 59.54 | 4 | 14.885 | 14.885 | 45 | 669.825 | 0.062021 | 2x200
CAFETARIA | 59.54 | 1.5 | 39.6933 | 39.6933 | 28.8 | 1143.168 | 0.10585 | 2x300
SALLE A MANGER | 47 | 1.5 | 31.3333 | 32 | 28.8 | 921.6 | 0.085333 | 2x250
DRESS ROOM 1 | 9.61 |  |  |  |  | 36 | 0.0033333 | 100
DRESS ROOM 2 | 9.61 |  |  |  |  | 36 | 0.0033333 | 100
1ST FLOOR
ZONE 1 | 428.83 | 15 | 28.5887 | 29 | 45 | 1305 | 0.12083 | 6X160
ZONE 2 | 126.26 | 15 | 8.4173 | 9 | 45 | 405 | 0.0375 | 4X125
BUREAU | 23.32 | 15 | 1.5547 | 2 | 45 | 90 | 0.0083333 | 125
SANIT HOMMES | 6.77 |  |  |  |  | 36 | 0.0033333 | 100
SANIT P.M.R. | 3.11 |  |  |  |  | 36 | 0.0033333 | 100
SANIT DAMES | 6.94 |  |  |  |  | 36 | 0.0033333 | 100
SMALL KITCHENETTE | 2.94 |  |  |  |  | 36 | 0.0033333 | 100
2ST FLOOR
ZONE 1 | 428.83 | 15 | 28.5887 | 29 | 45 | 1305 | 0.12083 | 6X160
ZONE 2 | 126.26 | 15 | 8.4173 | 9 | 45 | 405 | 0.0375 | 4X125
BUREAU | 23.32 | 15 | 1.5547 | 2 | 45 | 90 | 0.0083333 | 125
SANIT HOMMES | 6.77 |  |  |  |  | 36 | 0.0033333 | 100
SANIT P.M.R. | 3.11 |  |  |  |  | 36 | 0.0033333 | 100
SANIT DAMES | 6.94 |  |  |  |  | 36 | 0.0033333 | 100
SMALL KITCHENETTE | 2.94 |  |  |  |  | 36 | 0.0033333 | 100
3ST FLOOR
ZONE 1 | 428.83 | 15 | 28.5887 | 29 | 45 | 1305 | 0.12083 | 6X160
ZONE 2 | 126.26 | 15 | 8.4173 | 9 | 45 | 405 | 0.0375 | 4X125
BUREAU | 23.32 | 15 | 1.5547 | 2 | 45 | 90 | 0.0083333 | 125
SANIT HOMMES | 6.77 |  |  |  |  | 36 | 0.0033333 | 100
SANIT P.M.R. | 3.11 |  |  |  |  | 36 | 0.0033333 | 100
SANIT DAMES | 6.94 |  |  |  |  | 36 | 0.0033333 | 100
SMALL KITCHENETTE | 2.94 |  |  |  |  | 36 | 0.0033333 | 100
4ST FLOOR
ZONE 1 | 428.83 | 15 | 28.5887 | 29 | 45 | 1305 | 0.12083 | 6X160
ZONE 2 | 126.26 | 15 | 8.4173 | 9 | 45 | 405 | 0.0375 | 4X125
BUREAU | 23.32 | 15 | 1.5547 | 2 | 45 | 90 | 0.0083333 | 125
SANIT HOMMES | 6.77 |  |  |  |  | 36 | 0.0033333 | 100
SANIT P.M.R. | 3.11 |  |  |  |  | 36 | 0.0033333 | 100
SANIT DAMES | 6.94 |  |  |  |  | 36 | 0.0033333 | 100
SMALL KITCHENETTE | 2.94 |  |  |  |  | 36 | 0.0033333 | 100

## Pipes Cataloque
PIPES SURFACE
Diameter (mm) | Surface (m²)
100 | 0.007854
125 | 0.012272
150 | 0.017671
160 | 0.020106
200 | 0.031416
250 | 0.049087
300 | 0.070686
315 | 0.077931
355 | 0.09898
400 | 0.12566
450 | 0.15904
500 | 0.19635
560 | 0.2463
630 | 0.31173
710 | 0.39592
800 | 0.50266
900 | 0.63617
1000 | 0.7854
1120 | 0.98521
1250 | 1.2272
1400 | 1.5394
1600 | 2.0106

## Pipes Ways Admission
VERTICAL ADMISSION PIPES
A |  |  |  | B |  |  | B'
Vertical admission | m² | Pipe (mm) |  | Vertical admission | m² | Pipe (mm) | Vertical admission | m² | Pipe (mm)
ROOF | 0.53136 | 900 |  | ROOF | 0.45778 | 800 | ROOF | 0.41285 | 1000
4th | 0.07259 | 315 |  | 4th | 0.06032 | 300 | 4th | 0.049087 | 250
3rd | 0.07259 | 315 |  | 3rd | 0.06032 | 300 | 3rd | 0.049087 | 250
2nd | 0.07259 | 315 |  | 2nd | 0.06032 | 300 | 2nd | 0.049087 | 250
1st | 0.07259 | 315 |  | 1st | 0.06032 | 300 | 1st | 0.049087 | 250
Groundfloor | 0.241 | 560 |  | Groundfloor | 0.2165 | 560 | Groundfloor | 0.2165 | 560
Total Admission Surface (m²)= |  |  | 1.402 | The main pipe will be Ø1400
Total Admission in groundfloor (m²)= |  |  | 0.4575
Total Admission in upper floors (m²)= |  |  | 0.182
HORIZONTAL ADMISSION PIPES
GROUNDFLOOR |  |  |  | 1ST/2ND/3RD/4TH FLOOR |  |  | ROOF
Pipe Section | m² | Pipe (mm) |  | 1A-2A | 0.072591 | 315 | MAIN COLLECTOR | 1400 |  | NO MOVER******
1A-2A | 0.241 | 560 |  | 2A-3A | 0.052484 | 300 | COLLECTOR A | 355 |  | Diameter (mm) | Surface (m²)
2A-3A | 0.19191 | 500 |  | 3A-4A | 0.032378 | 250 | COLLECTOR B | 560 |  | 100 | 0.007854
3A-4A | 0.14282 | 450 |  | 4A-5A | 0.020106 | 160 | COLLECTOR C | 630 |  | 125 | 0.012272
4A-5A | 0.11141 | 400 |  | 1B-2B | 0.060319 | 300 | COLLECTOR D | 355 |  | 150 | 0.017671
5A-6A | 0.091303 | 355 |  | 2B-3B | 0.040212 | 250 |  |  |  | 160 | 0.020106
6A-7A | 0.079031 | 355 |  | 3B-4B | 0.020106 | 160 |  |  |  | 200 | 0.031416 | 0.241
7A-8A | 0.047615 | 250 |  | 1B'-2B' | 0.049087 | 250 |  |  |  | 250 | 0.049087
8A-9A | 0.035343 | 250 |  | 2B'-3B' | 0.036816 | 250 |  |  |  | 300 | 0.070686
9A-10A | 0.017671 | 150 |  | 3B'-4B' | 0.024544 | 200 |  |  |  | 315 | 0.077931
1B-2B | 0.21648 | 560 |  | 4B'-5B' | 0.012272 | 125 |  |  |  | 355 | 0.09898
2B-3B | 0.2042 | 560 | [7 empty] | 400 | 0.12566
3B-4B | 0.17279 | 500 | [7 empty] | 450 | 0.15904
4B-5B | 0.14137 | 450 | [7 empty] | 500 | 0.19635
5B-6B | 0.070686 | 300 | [7 empty] | 560 | 0.2463
[10 empty] | 630 | 0.31173
[10 empty] | 710 | 0.39592
[10 empty] | 800 | 0.50266
[10 empty] | 900 | 0.63617
[10 empty] | 1000 | 0.7854
[10 empty] | 1120 | 0.98521
[10 empty] | 1250 | 1.2272
[10 empty] | 1400 | 1.5394
[10 empty] | 1600 | 2.0106

## Pipes Ways Extraction
Extraction in toilets and changing rooms in groundfloor= 0,0033 m² x 11 | [5 empty] | 0.0363
Extraction in toilets and changing rooms in upper floors= 0,0033 m² x 7 | [5 empty] | 0.0231 |  | Diameter (mm) | Surface (m²)
[8 empty] | 100 | 0.007854
Admission in groundfloor= |  |  | 0.4575 |  |  |  |  | 125 | 0.012272
Admission in upper floors= |  |  | 0.182 |  |  |  |  | 150 | 0.017671
[8 empty] | 160 | 0.020106
Extraction needed in groundfloor= |  |  | 0.4212 |  | Specially for the kitchen I'm going to use a Ø450 extraction, |  |  | 200 | 0.031416
Extraction needed in upper floors= |  |  | 0.1589 |  | so I will need more extraction points in the groundfloor= |  | 0.26216 | 250 | 0.049087
[8 empty] | 300 | 0.070686
No. of extraction points needed per diameter | [7 empty] | 315 | 0.077931
GROUNDFLOOR (0,2622) |  | UPPER FLOORS (0,1589) | [5 empty] | 355 | 0.09898
125 | 21.3624 | 125 | 12.9481 |  |  |  |  | 400 | 0.12566
150 | 14.835 | 150 | 8.9918 |  |  |  |  | 450 | 0.15904
160 | 13.0386 | 160 | 7.9029 |  |  |  |  | 500 | 0.19635
200 | 8.3447 | 200 | 5.0579 |  |  |  |  | 560 | 0.2463
250 | 5.3406 | 250 | 3.237 |  |  |  |  | 630 | 0.31173
300 | 3.7087 | [6 empty] | 710 | 0.39592
[8 empty] | 800 | 0.50266
I decide to take 250x6 for the groundfloor | [7 empty] | 900 | 0.63617
I decide to take 150x9 for the upper floors | [7 empty] | 1000 | 0.7854
EXTRACTION PIPES
[8 empty] | 1120 | 0.98521
GROUNDFLOOR |  |  |  | TOILETS |  |  |  | 1250 | 1.2272
Pipe Section | m² | Pipe (mm) |  | Pipe Section | m² | Pipe (mm) |  | 1400 | 1.5394
1C-2C | 0.13108 | 450 |  | 1T-2T | 0.007854 | 100 |  | 1600 | 2.0106
2C-3C | 0.049087 | 250 |  | 2T-5T | 0.015708 | 150
2C-4C | 0.081991 | 355 |  | 3T-4T | 0.007854 | 100
4C-5C | 0.032903 | 250 |  | 4T-5T | 0.015708 | 150
1C'-2C' | 0.13108 | 450 |  | 5T-6T | 0.031416 | 200
2C'-3C' | 0.081991 | 355 |  | 6T-7T | 0.03927 | 250
3C'-4C' | 0.032903 | 250 |  | 7T-8T | 0.047124 | 250
kitchen | 0.14137 | 450 |  | 8T-9T | 0.054978 | 300
1ST/2ND/3RD/4TH FLOOR |  |  |  | CHANGING ROOM
1C-2C | 0.12355 | 400 |  | 1R-2R | 0.007854 | 100
2C-3C | 0.10588 | 400 |  | 2R-5R | 0.015708 | 150
3C-4C | 0.088212 | 355 |  | 3R-4R | 0.007854 | 100
4C-5C | 0.07054 | 300 |  | 4R-5R | 0.015708 | 150
5C-6C | 0.052869 | 300 |  | 5R-6R | 0.031416 | 200
6C-7C | 0.035197 | 200
7C-8C | 0.017526 | 150
1D-2D | 0.035343 | 250
2D-3D | 0.017671 | 150
ROOF
MAIN COLLECTOR |  | 1400
COLLECTOR A |  | 630
COLLECTOR B |  | 710
COLLECTOR C |  | 1000
COLLECTOR D |  | 1000